## Table 1
Sub: Coal Or Commercial-Filing of Petition for 5 Control Period (2024-29) and True-up Petition before Hon’ble TSERC -certain information -Req. - Reg. Ref: 1. Draft TSERC (MYT) Regulations, 2023. 2. Lr. No. CE (Coal dr Commercial)/ SE(C&C)/ F. MYT (2024-29)/ D.No. 124/23, Dt: 06.06.2023.

## Table 2
Hon’ble TSERC has hosted the Draft TSERC (MYT) Regulations, 2023 on Dt: 16.11.2023. As per the Draft TSERC (MYT) Regulations, 2023, the Petition under MYT by the Generating entity shall be filed with Hon’ble TSERC before Dt: 02.01.2024 and comprising of the following i. True- np of proceeding year for Generation Business, ii. True- np of proceeding year for Integrated Mine, iii. Proposal of Tariff for each year of the Control Period for Generation Business, iv. Proposal of Input price of coal supplied from integrated mine for each year of the Control Period. Further, as per the Provisions No.29 of Draft TSERC (MYT) Regulation, 2023 delay in submission of Tariff / True-up filings, rate of ROE shall be reduced by 0.5% per month or part thereof. In this regard, Hon’ble TSERC vide mail Dt: 21.12.2023 has communicated the formats for filling the MYT Petition. The formats in soft and hard copies pertaining to your wing are here with enclosed. It is requested to furnish the information station-wise as per Annexure-I (Enclosed) and Financial year-wise (From FY 2022-23 to FY 2028-29) in the formats enclosed in soft and hard copies by Dt: 29.12.2023 so as to enable this office for filing the MYT (2024-29) and True-up Petition. “Matter may please be treated as most urgent” Encl: Format Nos: Form: 2.3, 3, 3.1, 9 and 18.

## Table 3
Chief En vil**" neer Coal A Commercial

## Table 4 (hidden)
To The Chief Engineer (HPC&HP)/TSGENCO/VS/HYD U.O.No: CE (Coal &Comm1. )/ SE(C&C)/F.MYT (2024-29)/ D.No: L 9 /23, Dtd. Ł1 .12 .2023.
TELANGANA ATE P WER GENEnATION CORPORATION LIMITED
Chief @ ”
TSGEN
{@gg‹gypgj Hyderąbad-500082
‹?«ty:&dis4s08Ż9 /847
19?1
d£fHO•ll
O/o the Chief Engineer Coal & Commercial,
VidyutSoudha, Hyderabad.
U.O to CE HPC&HP

## Table 6 (hidden)
(Rs. Crore)

## Form 2.3
NSHES, Nagaejunasagar NSPH & NSLCPH Form 2.3: Repair & Maintenance Expenses
(Rs. In crores)
S. NO. |  | 2019-20 | 2020-21 | 2021-22 | 2022-23 | Current Year 'n' 2023-24 |  |  | Control period
|  | Apr-Mar | Apr-Mar | Apr-Mar | Apr-Mar | Apr-sep | Oct-Mar | Apr-Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 |  | 2028-29
|  | Audited | Audited | Audited | Audited | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected |  | Projected
1 | Plant & Machinery | 2.4805 | 8.3052 | 3.4466 | 2.6066 | 1.3881 | 5.6944 | 7.0825 | 7.287 | 8.0157 | 8.8173 | 9.699 |  | 10.6689
2 | Buildings | 0.0893 | 0.13974 | 0.073908 | 0.21875 | 0.31244 | 1.51 | 1.8224 | 2.42 | 2.662 | 2.9282 | 3.221 |  | 3.5431
3 | Civil Works | 1.6944 | 0.6893 | 0.91176 | 1.3172 | 1.2778 | 2.07 | 3.3478 | 1.81 | 1.991 | 2.1901 | 2.4091 |  | 2.65
4 | Hydraulic Works | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
5 | Lines & Cable Networks | 0.0632 | 0.023498 | 0.12527 | 0.0046419 | 0.086713 | 0.557 | 0.64371 | 0.21 | 0.231 | 0.2541 | 0.27951 |  | 0.30746
6 | Vehicles | 0.0183 | 0.025853 | 0.0082553 | 0.015721 | 0.00082378 | 0 | 0.00082378 | 0 | 0 | 0 | 0 |  | 0
7 | Furniture & Fixtures | 0.0001 | 0.000921 | 0.000529 | 0.0054079 | 0.00024 | 0.060057 | 0.060297 | 0.13 | 0.143 | 0.1573 | 0.17303 |  | 0.19033
8 | Office Equipment | 0.0874 | 0.029832 | 0.032539 | 0.013141 | 0.0068253 | 0 | 0.0068253 | 0 | 0 | 0 | 0 |  | 0
9 | Gross R&M Expenses | 4.4332 | 9.2143 | 4.5989 | 4.1815 | 3.073 | 9.8915 | 12.9645 | 11.857 | 13.0427 | 14.347 | 15.7817 |  | 17.3598
10 | Gross Fixed Assets at beginning of year | 1941.7299 | 1942.2368 | 1943.0485 | 1949.2851 | 1949.2849 | 0 | 1949.2849 | 1949.2849 | 1949.2849 | 1949.2849 | 1949.2849 | 1949.2849 | 1949.2849
11 | R&M Expenses as °/» of GFA at beginning of year | 0.22831 | 0.47442 | 0.23668 | 0.21451 | 0.15765 |  | 0.66509 | 0.60827 | 0.67 | 0.74 | 0.74 | 0.81 | 0.89

## Table 8 (hidden)
TSERC - MYT 2023 Petition Formats - Generation (Page set-up)

## Table 9 (hidden)
<Name of the Generating Entity> <Name of the Generating Stations Form 3: Summary of Capital Expenditure and Capitalisation

## Table 10 (hidden)
(Rs. Crore)

## Form 3
NSHES, Nagarjunasagar
NSPH & NSLCPH
|  | Form 3: Summary of Capital Expenditure and Capitalisation | [10 empty] | (Rs. Crore)
s. NO | Particulars | Year (n-1) |  |  | Current Year 'n' |  |  |  | Control Period
|  | MYT/Tariff Order | Apr-Mar | True-Up requirement | MYT/Tariff Order | Apr-Sep | Oct-Mar | Apr - Mar | n+1 | n+2 | n+3 | n+4 | n+5
|  | Approved | Audited | Claimed | Approved | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Opening Capital Works in Progress |  | 0.86697 |  |  | 0.87 | 0 | 0.87 | 24.43 | 26.55 | 19.75 | 0.6 | 22.6822
2 | Capital Expenditure during the year |  | 0.011636 |  |  | 0 | 2.09 | 2.09 | --- | --- | --- | --- | ---
3 | Capitalisation during the year |  | 0.011636 |  |  | 0 | 0 | 0 | --- | --- | --- | --- | ---
4 | Closing Capital Works In Progress |  | 0.86697 |  |  | 0.87 | 2.09 | 2.96 | --- | --- | --- | --- | ---

## Form 3.1
NAGARJUNASAGAR HYDRO ELECTRIC SCHEME, NAGARJUNASAGAR
NSPH & NSLCPH
Form 3.1: Statement of Additional Capitalisation after COD (In CRORES)
S. No | F.Y Current year n : 2023-24 | Name of the Pakage (BTG,BOP,CIVIL works Etc.,) | Name of the work | Total Estimated Cost* (RS.Crore) | Capital Expenditure during the year(Rs. Crore) | Capitalisation during the year (Rs. Crore) | Asset group under which the capitalisation has been accounted (Land,Buildings Etc.,) | Scope of Work | Relevant clauses of the TSERC MYT Regulation,2023 under which the capitalistion has been claimed | Justification
Year (n-1) (2022-23)
Nil
Current Year 'n' (2023-24)
1 | 2023-24 | NSHES (O&M) | Procurement of 220KV Decentralized Main-I & Main II Bus Bar Protection Scheme. | 1.51 |  |  |  | Procurement of 220KV Decentralized Main-I & Main II Bus Bar Protection Scheme. |  | As per Protection Audit Recommendations
2 | 2023-24 | NSHES (O&M) | Procurement of vehicles | 0.23 |  |  |  | Procurement of vehicles
3 | 2023-24 | NSHES (O&M) | Stop log gates: Reconditioning of 18 No's stop log gates,Stop log Groove checking of 1 No of Unit, Videography, Insertion of 18 No's Stop Log gate elements in Unit-1 stop log groove and complete sealing of elements | 0.35 |  |  |  | Stop log gates: Reconditioning of 18 No's stop log gates,Stop log Groove checking of 1 No of Unit, Videography, Insertion of 18 No's Stop Log gate elements in Unit-1 stop log groove and complete sealing of elements |  | Upgradation of the present system
| Total (2023-24) |  |  | 2.09
Current Year 'n+1' (2024-25)
1 | 2024-25 | NSHES (O&M) | Procurement of New Guide vae Apparatus for Unit-1(110MW,Make BHEL) | 12.36 |  |  |  | --- |  | Upgradation of the present system
2 | 2024-26 | NSHES (O&M) | 2nd Capital Overhaul of Turine and its auxiliaries of Unit-1(110 MW,make:BHEL) | 1.5 | [5 empty] | AS Capital Works scheduled for every 20 years
3 | 2024-27 | NSHES (O&M) | Procurement of control cables for Main-I&Main-II Bus bar Protection panels | 1.2 |  |  |  | --- |  | Upgradation of the present system
4 | 2024-25 | NSHES(CIVIL) | NSHES - O&M –CSDII- Design, Manufacture, Supply, Delivery, Erection and commissioning of Advanced surface water treatment plant (Micro filters) along with UV/Chlorination treatment with capacity of 18 m3/hr ( 0.3 MLD) to treat surface water for potable need at Pylon, Nagarjunasagar and Construction of Micro filter Room of size 4m x 6m at B Colony, Pylon, Nagarjunasagar | 0.44 |  |  |  | NSHES - O&M –CSDII- Design, Manufacture, Supply, Delivery, Erection and commissioning of Advanced surface water treatment plant (Micro filters) along with UV/Chlorination treatment with capacity of 18 m3/hr ( 0.3 MLD) to treat surface water for potable need at Pylon, Nagarjunasagar and Construction of Micro filter Room of size 4m x 6m at B Colony, Pylon, Nagarjunasagar |  | The water treatment plant of capacity 10.0m3/hr (0.20MLD) was installed for supply of water to both A and B Colonies at Pylon in NSHES Complex. But as per field observation the existing water treatment plant is not sufficient for supply of purified water to both A& B Colonies. Hence, another water treatment plant of capacity 18.0m3/hr (0.30MLD) is proposed to cater the demand of purified water supply to A&B Colonies in NSHES.
5 | 2024-25 | NSHES(CIVIL) | NSHES - Supply and fixing of 100 mm new G.I line B-class in place of damaged one from Filter House to B-Colony. | 0.38 |  |  |  | NSHES - Supply and fixing of 100 mm new G.I line B-class in place of damaged one from Filter House to B-Colony. |  | The water to the colonies is being drawn from penstock to B- colony filter house along El+420 road. At present water is being drawing thrugh HDPE pipe line of 1.5KM long which was laid in 2015. There is also one A.C. pipe line which is age old one and having many repairs. Whenver level in the reservoir falls the water is also being drawing through A.C. Pipe line. Some parts of AC pipe line were replaced with new GI pipe lines when ever there was disruption in water supply to the Colonies, Vidyuth Sadan Guest House, DAV School, Hospital and Administrative Building in NSHES. The AC pipe line is frequently getting damaged and attending the repair to the pipe line is very cumbersome and causes delay in water supply restoration works. Hence it is proposed for laying of new G.I pipe line with controlling valves at regular intervals for supply of water to the filter house at B Colony. Further the water supply lines from fileter house at B Colony to sump at A Colony are also age old AC lines and proposed for laying of new G.I line.
6 | 2024-25 | NSHES(CIVIL) | NSHES-Rectification, erection, testing and commisssioning of existing stop log gates and its grooves including Design, Supply, Fabrication, Erection and commissioning of Monorail hoist and its supporting structure for stop log gates at Nagarjunasagar Left Canal Power House . | 1.72 |  |  |  | NSHES-Rectification, erection, testing and commisssioning of existing stop log gates and its grooves including Design, Supply, Fabrication, Erection and commissioning of Monorail hoist and its supporting structure for stop log gates at Nagarjunasagar Left Canal Power House . |  | There are no existing stop log gates for NSLCPH Power House. If the stop log gates are not provided, during de-lifting of penstock gates any difficulty arises, the only option is to shut down the units till the reservoir level reduces and disconnects the Power House Surge pool from the reservoir for attending the repairs to Penstock gates. If any repairs are to be taken up for machinery inside the unit when there is repair of penstock gates it is necessary to use of stoplog gates to stop the water entering inside the power house. In absence of stop log gates, any emergency repairs can not be be carried out on Penstock gates there by causing hindrance in Power Generation. Estimate is submitted to the Head Quarters vide Lr.No.CE/o&M/NSHES/De.Tech&Pur/ADET/AET/F.HO/D.No.767/22, Dt.24.09.2022
7 | 2024-25 | NSHES(CIVIL) | NSHES-Construction of One 'D' type block consisting of 7 Nos ADE Type Quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar | 4.5 |  |  |  | NSHES-Construction of One 'D' type block consisting of 7 Nos ADE Type Quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar |  | Consent is issued for construction of Residential Quarters of D Type-7 Nos in the area available at 'A' Colony duly adopting the floor plans and specifications issued vide G.O.O . No.456/CE/Civil/Thermal/2020, dated 03.03.2020 vide Lr.No. ED/C/Hydel/SE/HD-II/C&I/F.E Type Quartres/D.No.80/23, Dt.01.06.2023
8 | 2024-25 | NSHES(CIVIL) | NSHES - O&M – Construction of new office building for ADE/O&M/NSLH & workshop adjacent to service bay at NSLCPH | 0.23 |  |  |  | NSHES - O&M – Construction of new office building for ADE/O&M/NSLH & workshop adjacent to service bay at NSLCPH |  | Consent is issued for construction of Office Buildign to ADE/O&M/NSLCPH at NSLCPH during the visit of Directr Hydel to NSHES on 16.07.2023 and approved drawings are issued vide Lr.No.ED/C/Hydel/SE-II/HD-II/F.NSHES/D.no.174/2022-23, Dt.31.03.2023
9 | 2024-25 | NSHES(CIVIL) | NSHES - NSTPD - Acquisition of Patta lands Ac. 4.37 gts in Sy. No. 33 in Nadigadda H/o Chityala Village of Adavidevulapally Mandal, Ac.14.28 gts in Sy.No. 14& 16 of Thunikinuthala village of T.Sagar Mandal and toatl is about to AC 19.25 gts | 1.8 |  |  |  | NSHES - NSTPD - Acquisition of Patta lands Ac. 4.37 gts in Sy. No. 33 in Nadigadda H/o Chityala Village of Adavidevulapally Mandal, Ac.14.28 gts in Sy.No. 14& 16 of Thunikinuthala village of T.Sagar Mandal and toatl is about to AC 19.25 gts |  | The Patta lands Ac. 4.37 gts in Sy. No. 33 in Nadigadda H/o Chityala Village of Adavidevulapally Mandal, Ac.14.28 gts in Sy.No. 14& 16 of Thunikinuthala village of T.Sagar Mandal and total is about to AC 19.25 gts are submerged in NSTPD reservoir. The Acquisition of the land under process. The approximate cost of land is taken as Rs.12 Lakhs per 1 Acre
10 | 2024-25 | NSHES(CIVIL) | NSHES - NSTPD - Acquisition of Patta lands in Sy. No. 19 at Chityala village, Adavidevulapally Mandal is about to AC 2.23 Gts | 0.3 |  |  |  | NSHES - NSTPD - Acquisition of Patta lands in Sy. No. 19 at Chityala village, Adavidevulapally Mandal is about to AC 2.23 Gts |  | The payment for Ac.2.23 Gts is pending due to court case. The Revenue Department has informed that the court case is cleared and requested to submit fresh requisition. The approximate cost is taken as Rs.12 Lakhs per 1 Acre.
| Total (2024-25) |  |  | 24.43
Current Year 'n+2' (2025-26)
1 | 2025-26 | NSHES (O&M) | Procurement of 1No. Single Phase 45 MVA, 13.8KV/220/√3KV, 50Hz, OFW cooling M/s BHEL Make Generator Transformer for NSPH of TSGENCO, NagarjunaSagar. | 4.25 |  |  |  | Procurement of 1No. Single Phase 45 MVA, 13.8KV/220/√3KV, 50Hz, OFW cooling M/s BHEL Make Generator Transformer for NSPH of TSGENCO, NagarjunaSagar. |  | Upgradation of the present system
2 | 2025-26 | NSHES (O&M) | Procurement of 1No. Single Phase 42.5 MVA, 11KV/220√3KV,50Hz, OFW cooling M/s TELK Make Generator Transformer for NSPH of TSGENCO, NagarjunaSagar. | 4 |  |  |  | Procurement of 1No. Single Phase 42.5 MVA, 11KV/220√3KV,50Hz, OFW cooling M/s TELK Make Generator Transformer for NSPH of TSGENCO, NagarjunaSagar. |  | Upgradation of the present system
3 | 2025-26 | NSHES (O&M) | Supply, errection and commissioning of 220KV Switchyard equipment for SFC (Static Frequency Convertor) | 8 |  |  |  | Supply, errection and commissioning of 220KV Switchyard equipment for SFC (Static Frequency Convertor) |  | Upgradation of the present system
4 | 2025-26 | NSHES (O&M) | Procurement of Relay panel for 30MVA Station Transformer at NSPH | 0.3 |  |  |  | Procurement of Relay panel for 30MVA Station Transformer at NSPH |  | As per Protection Audit Recommendations
1 | 2025-26 | NSHES(CIVIL) | NSHES-Construction of One 'C' type block consisting of 10 Nos DE Type Quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar | 5 |  |  |  | NSHES-Construction of One 'C' type block consisting of 10 Nos ADE Type Quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar |  | Consent is issued for construction of Residential Quarters of C Type-10 Nos in the area available at 'A' Colony duly adopting the floor plans and specifications issued vide G.O.O . No.456/CE/Civil/Thermal/2020, dated 03.03.2020 vide Lr.No. ED/C/Hydel/SE/HD-II/C&I/F.E Type Quartres/D.No.80/23, Dt.01.06.2023
2 | 2025-26 | NSHES(CIVIL) | NSHES – NSTPD - Removal of hard rock outcrop for deepening of existing channel up to EL+71.00m by control blasting method on the d/s of TRC trash racks at Main Power House. | 5 |  |  |  | NSHES – NSTPD - Removal of hard rock outcrop for deepening of existing channel up to EL+71.00m by control blasting method on the d/s of TRC trash racks at Main Power House. |  | The existing hard rock outcrops on the u/s of the trash racks at TRC at Main Power House are required to be removed and the channel to be deepened to EL+71.00m to improve the flow conditions and thereby allowing sufficient water to all the units for running the 7- units in pumping mode, simultaneously.
| Total (2025-26) |  |  | 26.55
Current Year 'n+3' (2026-27)
1 | 2026-27 | NSHES (O&M) | Purchase of spares for KMW mechanical Governor of unit-2 at NSLCPH | 0.25 |  |  |  | Purchase of spares for KMW mechanical Governor of unit-2 |  | Upgradation of the present system
2 | 2026-27 | NSHES (O&M) | Capital Overhaul of Unit-2 turbine and its auxiliaries at NSLCPH | 0.5 |  |  |  | Capital Overhaul of Unit-2 turbine and its auxiliaries |  | Upgradation of the present system
3 | 2026-27 | NSHES(CIVIL) | NSHES-Construction of One 'B' type block consisting of 2 Nos SE Type Quarters and one block consisting of 8 Nos of E Type quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar | 2.5 |  |  |  | NSHES-Construction of One 'B' type block consisting of 2 Nos SE Type Quarters and one block consisting of 8 Nos of E Type quarters for the staff of NSHES at A Colony, Pylon, Nagarjunasagar |  | Consent is issued for construction of Residential Quarters of C Type-10 Nos in the area available at 'A' Colony duly adopting the floor plans and specifications issued vide G.O.O . No.456/CE/Civil/Thermal/2020, dated 03.03.2020 vide Lr.No. ED/C/Hydel/SE/HD-II/C&I/F.E Type Quartres/D.No.80/23, Dt.01.06.2023
4 | 2026-27 | NSHES(CIVIL) | NSHES- NSTPD- rehabilitization and Resettlement- Acquisition of houses falling below 100.0m distance from FRL +75.5m in Jalakoti thanda, Nadigadda and Chityala villages | 16.5 |  |  |  | NSHES- NSTPD- rehabilitization and Resettlement- Acquisition of houses falling below 100.0m distance from FRL +75.5m in Jalakoti thanda, Nadigadda and Chityala villages
| Total (2026-27) |  |  | 19.75
Current Year 'n+4' (2027-28)
1 | 2027-28 | NSHES (O&M) | Penstock Gates: Reconditioning of penstock gates that includes seals replacement, rollers replacement, sand blasting and painting, penstock guide track checking and repair, power pack overhauling | 0.6 |  |  |  | Penstock Gates: Reconditioning of penstock gates that includes seals replacement, rollers replacement, sand blasting and painting, penstock guide track checking and repair, power pack overhauling |  | Upgradation of the present system
| Total (2027-28) |  |  | 0.6
Current Year 'n+5' (2028-29)
1 | 2028-29 | NSHES (O&M) | Replacement/retrofit of Old control panels with new control panels of SAB-I to IV and Reserve Board and Units-1 to Unit-8 UAB 's and electrical wiring and replacement of 2000A Isolators at NSPH of NSHES . | 1 |  |  |  | Replacement/retrofit of Old control panels with new control panels of SAB-I to IV and Reserve Board and Units-1 to Unit-8 UAB 's and electrical wiring and replacement of 2000A Isolators at NSPH of NSHES . |  | Upgradation of the present system
2 | 2028-29 | NSHES (O&M) | Procurement of Generator Protection panels for Unit-1,Unit-2 and C&R Panel for two no of 132KV feeders at NSLCPH | 0.7 |  |  |  | Procurement of Generator Protection panels for Unit-1,Unit-2 and C&R Panel for two no of 132KV feeders at NSLCPH |  | As per Protection Audit Recommendations
3 | 2028-29 | NSHES (O&M) | Procurement of 2Nos protection panel for 100MVA 220/132KV Power transormers,1No Control relay panel for 7.5MVA 132/11KV Power transformer and 1 no disturbance recorder(DR)evaluation unit at 220KVRS of NSHES | 0.4322 |  |  |  | Procurement of 2Nos protection panel for 100MVA 220/132KV Power transormers,1No Control relay panel for 7.5MVA 132/11KV Power transformer and 1 no disturbance recorder(DR)evaluation unit at 220KVRS of NSHES |  | As per Protection Audit Recommendations
4 | 2028-29 | NSHES (O&M) | Procurement of primary injection test kit | 0.15 |  |  |  | Procurement of primary injection test kit |  | Upgradation of the present system
5 | 2028-29 | NSHES (O&M) | Procurement of universAL RELAY TEST KIT | 0.4 |  |  |  | Procurement of universAL RELAY TEST KIT |  | Upgradation of the present system
6 | 2028-29 | NSHES (O&M) | Procurement of 2Nos new Digital Governor Control Panels for Unit-2& 8 | 20 |  |  |  | Procurement of 2Nos new Digital Governor Control Panels for Unit-2& 8 |  | Upgradation of the present system
22.6822

## Form 9
NSHES, Nagarjunasagar
NSPH & NSLCPH
Form 9: Planned & Forced Outages
S.No. | Particulars | Year (n-1) | Current Year ’n’(2023-24) |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | n+1 | n+2 | n+3 | n+4 | n+5
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 1
A. | Planned Outages
| No of days of outage | [5 empty] | 180 DAYS
| Period of Outage | [5 empty] | JAN-JUNE
| Reasons for Outage | Asper the statement Enclosed |  |  |  |  | Capital Overhauling works
Annexure
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
2 | Unit 2
A. | Planned Outages
| No of days of outage | [8 empty] | 30 DAYS
| Period of Outage | [8 empty] | JAN
| Reasons for Outage | [8 empty] | Annual Maintenace works
B. | Forced Outages
| No of days of outage |  |  |  | 90 DAYS
| Period of Outage |  |  |  | JAN-MARCH
| Reasons for Outage |  |  |  | For Arresting TGB vibrations
3 | Unit 3
A. | Planned Outages | [8 empty] | 60 DAYS
| No of days of outage |  |  |  |  | 30 DAYS |  |  |  | APR-MAY
| Period of Outage |  |  |  |  | FEB-01 to MARCH-02 |  |  |  | Annual Maintenace works
| Reasons for Outage | Asper the statement Enclosed |  |  |  | Annual Maintenace works
Annexure
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
4 | Unit 4
A. | Planned Outages
| No of days of outage | [6 empty] | 90 DAYS | 60 DAYS
| Period of Outage | [6 empty] | APR-JUNE | MAY-JUNE
| Reasons for Outage | [6 empty] | Annual Maintenace works | Annual Maintenace works
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
5 | Unit 5
A. | Planned Outages
No of days of outage
Period of Outage
Reasons for Outage
Asper the statement Enclosed
B. | Forced Outages | Annexure
| No of days of outage | [6 empty] | 60 DAYS
| Period of Outage | [6 empty] | MAR-APR
| Reasons for Outage | [6 empty] | Annual Maintenace works
6 | Unit 6
A. | Planned Outages
| No of days of outage |  |  |  |  | 60 DAYS
| Period of Outage |  |  |  |  | MAR-APR
| Reasons for Outage |  |  |  |  | Annual Maintenace works
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
7 | Unit 7
A. | Planned Outages
| No of days of outage | [6 empty] | 60 DAYS
| Period of Outage | [6 empty] | JAN-FEB
| Reasons for Outage | [6 empty] | Annual Maintenace works
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
8 | Unit 8
A. | Planned Outages
| No of days of outage |  |  |  |  | 31 DAYS |  |  |  | 60 DAYS
| Period of Outage |  |  |  |  | JAN |  |  |  | FEB-MARCH
| Reasons for Outage | Asper the statement Enclosed |  |  |  | Annual Maintenace works |  |  |  | Annual Maintenace works
Annexure
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage

## 2023-24
Unit Outages Data of Nagarjuna Sagar Power House , Nagarjunasagar
|  |  | Name of the hydro Electric Station |  |  |  |  | N.S.Power House, Nagarjuna Sagar | [5 empty] | YEAR : |  | 2023-24
|  | Organisation | [5 empty] | TSGENCO
NSPH : Units Outage Details
Intr No | Unit No. | Planned Outage |  |  |  | Planned Outage Duration | Outage Code | Forced Outage |  |  |  | Forced Outage Duration | Outage Code | Planned + Forced Duration | Energy Loss (MWH) | Brief description of Planned/ Forced outage & Remarks
|  | From |  | To |  |  |  | From |  | To
|  | Date | Time | Date | Time |  |  | Date | Time | Date | Time
1 | 5 | [6 empty] | 15.04.2023 | 7:17 | 15.04.2023 | 11:25 | 4:08 | -- | 0.17222 |  | LC issued on Unit-5 to attend Hotspot Complaint on CB-52 R-Phase pole Top terminal Moose Conductor, as the temperature observed above >275°
2 | 7 | 2023-04-24 | 10:06 | 2023-04-30 | 24:00 | 157:54 | [7 empty] | 1900-01-05 13:54 |  | LC issued on Unit-7 for carrying out maintenance works of Thrust Bearing oil coolers & Inspection of Thrust Bearing Pads and Inspection & cleaning of Stator winding, NGT,UAT & LAPT cubicle.
| 7 | 2023-05-01 | 0:00 | 2023-05-31 | 24:00 | 1900-01-30 | [7 empty] | 1900-01-30 |  | LC issued on Unit-7 for carrying out maintenance works of Thrust Bearing oil coolers & Inspection of Thrust Bearing Pads and Inspection & cleaning of Stator winding, NGT,UAT & LAPT cubicle.
| 3 | [6 empty] | 2023-05-09 | 9:44 | 2023-05-10 | 19:50 | 1899-12-31 10:06 |  | 1899-12-31 10:06 |  | To attend the compalint on " compressor running for long time and CB-52 Trip circuit -1 & 2 Faulty alarm observed even though DC supply is ON.
| 1 | [6 empty] | 2023-05-16 | 22:02 | 2023-05-16 | 23:18 | 0.052778 |  | 0.052778 |  | On 16-05-2023 at 22:02 While Units 1,2,3,4,5,6, 8. Units 1,3,5 & TPF-I are tripped & Bus-A dead due to Bus Bar Protection and CT Neutral wire continuty missed.
| 3 | [6 empty] | 2023-05-16 | 22:02 | 2023-05-16 | 23:18 | 0.052778 |  | 0.052778 |  | On 16-05-2023 at 22:02 While Units 1,2,3,4,5,6, 8. Units 1,3,5 & TPF-I are tripped & Bus-A dead due to Bus Bar Protection and CT Neutral wire continuty missed.
| 5 | [6 empty] | 2023-05-16 | 22:02 | 2023-05-16 | 23:18 | 0.052778 |  | 0.052778 |  | On 16-05-2023 at 22:02 While Units 1,2,3,4,5,6, 8. Units 1,3,5 & TPF-I are tripped & Bus-A dead due to Bus Bar Protection and CT Neutral wire continuty missed.
| 7 | 2023-06-01 | 0:00 | 2023-06-16 | 0:18 | 1900-01-14 00:18 | [7 empty] | 1900-01-14 00:18 |  | LC issued on Unit-7 for carrying out maintenance works of Thrust Bearing oil coolers & Inspection of Thrust Bearing Pads and Inspection & cleaning of Stator winding, NGT,UAT & LAPT cubicle.
| 3 | [6 empty] | 2023-06-01 | 9:09 | 2023-06-06 | 22:18 | 1900-01-04 13:09 |  | 1900-01-04 13:09 |  | LC issued on Unit-3 for identification and Rectification of 95% Stator Earth Fault
| 4 | [6 empty] | 2023-06-03 | 6:10 | 2023-06-03 | 13:37 | 0.31042 |  | 0.31042 |  | LC issued on Unit-4 for R-phase and B-phase GTs' coolers checked and recorded 70°C temperature on WTI and OTI. So LC taken for removing and cleaning of coolers
| 1 | [6 empty] | 2023-06-13 | 22:14 | 2023-06-14 | 9:42 | 0.47778 |  | 0.47778 |  | Outage due to Oil over flow from OLU sump tank and Governor oil sump tank's oil level low
| 1 | [6 empty] | 2023-06-14 | 9:42 | 2023-06-14 | 16:10 | 0.26944 |  | 0.26944 |  | LC issued on Unit-1 for Replacement of damaged cup seals of closing servomotor
| 1 | 2023-06-19 | 9:03 | 2023-06-30 | 24:00 | 1900-01-10 14:57 | [7 empty] | 1900-01-10 14:57 |  | LC issued on Unit-1 for annual maintenance works of Turbine and its auxiliaries by Mechanical maintenance Division and for attending annual maintenance works, inspection and cleaning of stator winding and replacement of stator air coolers by Electrical Maintenance division.
| 1 | 2023-07-01 | 0:00 | 2023-07-31 | 24:00 | 1900-01-30 | [7 empty] | 1900-01-30 |  | LC issued on Unit-1 for annual maintenance works of Turbine and its auxiliaries by Mechanical maintenance Division and for attending annual maintenance works, inspection and cleaning of stator winding and replacement of stator air coolers by Electrical Maintenance division.
| 4 | [6 empty] | 2023-07-18 | 21:22 | 2023-07-18 | 22:37 | 0.052083 |  | 0.052083 |  | Outage due to, Unit got tripped on Bearing Temperature Very High alarm while unit in service as Generator.
| 5 | 2023-07-20 | 18:35 | 2023-07-21 | 21:34 | 1899-12-31 02:59 | [7 empty] | 1899-12-31 02:59 |  | LC issued on Unit-5 for arresting oil Leakages of Unit-5 Penstock gate Hydraulic Hoist power pack.
| 3 | 2023-07-24 | 12:14 | 2023-07-31 | 24:00 | 1900-01-06 11:46 | [7 empty] | 1900-01-06 11:46 |  | LC issued on Unit-3 for replacing of Penstock Intake gate lifting links.
| 4 | [6 empty] | 2023-07-29 | 19:43 | 2023-07-29 | 21:38 | 0.079861 |  | 0.079861 |  | Outagedue to sparks observed at carbon brushes (slipring area) while unit in service as Generator.
| 6 | 2023-07-31 | 9:15 | 2023-07-31 | 15:27 | 0.25833 | [7 empty] | 0.25833 |  | LC issued on Unit-6 to attend the complaint on 189S1 Isolator, for alignment of Y-Phase contacts by adjusting Phase coupling mechanism linkage pipe.
| 1 | 2023-08-01 | 0:00 | 2023-08-13 | 23:46 | 1900-01-11 23:46 | [7 empty] | 1900-01-11 23:46 |  | LC issued on Unit-1 for annual maintenance works of Turbine and its auxiliaries by Mechanical maintenance Division and for attending annual maintenance works, inspection and cleaning of stator winding and replacement of stator air coolers by Electrical Maintenance division.
| 3 | 2023-08-01 | 0:00 | 2023-08-10 | 18:44 | 1900-01-08 18:44 | [7 empty] | 1900-01-08 18:44 |  | LC issued on Unit-3 for replacing of Penstock Intake gate lifting links.
| 2 | [6 empty] | 2023-09-22 | 23:14 | 2023-09-23 | 12:15 | 0.54236 |  | 0.54236 |  | Outage due to Unit-2 Pole Discrepancey complaint
| 2 | 2023-09-30 | 9:50 | 2023-09-30 | 24:00 | 0.59028 | [7 empty] | 0.59028 |  | LC issued on Unit-2 for arresting Vibrations
| 2 | 2023-10-01 | 0:00 | 2023-10-31 | 24:00 | 1900-01-30 | [7 empty] | 1900-01-30 |  | LC issued on Unit-2 for “Arresting of machine vibrations” by Electrical Maintenance division.
| 1 | [6 empty] | 2023-10-19 | 6:46 | 2023-10-19 | 11:10 | 0.18333 |  | 0.18333 |  | Unit-1 bridge -1 failed fan capacitor repalced with new one by A&C maintenance sub division.
[8 empty] | 2023-10-19 | 16:21 | 2023-10-19 | 24:00 | 0.31875 |  | 0.31875
[8 empty] | 2023-10-20 | 0:00 | 2023-10-20 | 10:15 | 0.42708 |  | 0.42708
| 4 | 2023-10-22 | 13:07 | 2023-10-22 | 14:15 | 0.047222 | [7 empty] | 0.047222 |  | Unit-4 tripped due to GT-R-Phase OLTC Bucholz trip
| 5 | 2023-10-25 | 18:08 | 2023-10-29 | 15:30 | 1900-01-02 21:22 | [7 empty] | 1900-01-02 21:22 |  | Unit-5 tripped due to rotor earth fault satge-II
| 2 | 2023-11-01 | 0:00 | 2023-11-30 | 24:00 | 1900-01-29 | [7 empty] | 1900-01-29 |  | LC issued on Unit-2 for “Arresting of machine vibrations” by Electrical Maintenance division.
| 4 | 2023-11-01 | 9:07 | 2023-11-01 | 18:33 | 0.39306 | [7 empty] | 0.39306 |  | LC issued on Unit-4 for alignment of 189S1 Isolator by ODYARD maintenance sub- division.
|  | 2023-11-02 | 8:48 | 2023-11-02 | 15:49 | 0.29236 | [7 empty] | 0.29236 |  | LC issued on Unit-4 for alignment of 189S1 Isolator by ODYARD maintenance sub- division
| 8 | 2023-11-01 | 9:07 | 2023-11-01 | 18:27 | 0.38889 | [7 empty] | 0.38889 |  | LC issued on Unit-8 for alignment of 189S2 Isolator by ODYARD maintenance sub- division.
| 5 | [6 empty] | 2023-11-21 | 16:50 | 2023-11-21 | 18:45 | 0.079861 |  | 0.079861 |  | Unit-5 checked GOP oil level switch at Turbine floor by A&C maintenance sub division.
Formulas:
YEAR : = [Planned Outage Duration]+[Forced Outage Duration]

## Form 18 NSPH
TELANGANA STATE POWER GENERATION CORPORATION LIMITED NAGARJUNA SAGAR HYDRO ELECTRIC SCHEME Form 18 : Plant Characteristics (Hydel)
1. Location | NSHES, Nagarjunasagar
State/Distt. | Telangana, Nalgonda (dist.)
River | Krishna River
2. Diversion Tunnel
Size, shape | Size:10 x 25 Ft., Type Horse Shoe
Length | 2480 Ft.
3. Dam
Type | Masonry with earth dam on flanks.
Maximum dam height | 380 Feet
4. Spillway
Type | Radial Crest Gates
Crest level of spillway | EL 546 Feet
5. Reservoir
Full Reservior Level (FRL) | 590 feet
Minimum Oraw Down Level (MDDL) | 510 feet
Live storage (MCM) | 5372.25 MCM
6. Desilting Arrangement | Not applicable
Type | -
Number and Size | -
Particle size to be removed(mm) | -
7. Head Race Tunnel | Not applicable
Size and type | -
Length | -
Design discharge(Cumecs) | -
8. Surge Shaft
Type | Circular Pipe Air vents provided at 605 ft
Diameter | 0.9 M
Height | 80 Ft
9. Penstock/Pressure shafts
Type | Circular type / Steel lined
Diameter & Length | 16' diameter & 159 M
10. Power House
Type | Open Air
Installed capacity (No of units x MW) | 875.6 MW (8 Nos. (1x110 + 7x100.8) + 2x30)
Peaking capacity during lean period (MW) | 875.6 MW
Type of turbine | Francis Vertical (Reversible) Turbines
Rated Head(M) | 93.0 Mtrs.
Rated Discharge(Cumecs) | 137.5 Cumecs
11. Tail Race Tunnel | Open to River
Diameter, shape | Not applicable
Length | Not applicable
Minimum tail water level | Not applicable
12. Switchyard
Type of Switch gear | Outdoor Switchyard, High voltage switch gear
No. of generator bays | 8 Bays
No. of Bus coupler bays | 1 Bays
No. of line bays | 10 Bays
Note: Specify limitation on generation during specific time period on account of restriction(s) on water use due to irrigation, drinking water, industrial, environmental considerations etc.

## Form 9 LCPH
Nagarjuna Sagar Left Canal Power House
Form 9: Planned & Forced Outages
S.No. | Particulars | Year (n-1) | Current Year 'n' |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | n+1 (2024-25) | n+2 (2025-26) | n+3 (2026-27) | n+4 (2027-28) | n+5 (2028-29)
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 1
A. | Planned Outages
| No of days of outage | 24 | 152 | 31 | 31 | 91 | 91 | 91 | 91 | 122
| Period of Outage | 6.6.2022 to 30.6.2022 | 6.5.2023 to 5.10.2023 | 01.3.2023 to 31.3.2023 | 01.3.2023 to 31.3.2023 | 01.4.2024 to 30.6.2024 | 15.04.2025 to 15.07.2025 | 15.04.2026 to 15.07.2026 | 15.04.2027 to 15.07.2027 | 01.4.2028 to 31.7.2028
| Reasons for Outage | LC no.284 issued to carry annual overhaul works | PIG hydraulic cylinder reconditioning works of unit 1 | reconditioning of stuffing box, inner cover and shaft sleeve assembly of unit -1 at LCPH | reconditioning of stuffing box, inner cover and shaft sleeve assembly of unit -1 at LCPH | reconditioning of stuffing box, inner cover and shaft sleeve assembly of unit -1 at LCPH | Replacing all transformer cooling water pipelines from Turbine floor to Switch Yard, Valves & NRV | Replacing all dewatering discharge pipelines from draft tube floor to Switch Yard and Overhauling and replacing spares for all dewatering pumps. | Annual Overhauling of Unit-1 | Replacement of 24V Battery Bank
| No of days of outage | 31 |  |  |  | 91 | 122 | 122 | 122
| Period of Outage | 1.7.2022 to 31.7.2022 |  |  |  | 15.04.2024 to 15.07.2024 | 01.4.2025 to 31.7.2025 | 01.4.2026 to 31.7.2026 | 01.4.2027 to 31.7.2027
| Reasons for Outage | LC no.284 issued to carry annual overhaul works |  |  |  | Ventilation system- air washer tank, mist eliminators and pump erection works. | Replacement of 220V Battery Bank | AVR to DVR of Unit-1 | Overhauling of GTR-1 & GTR-2
| No of days of outage | 13 |  |  |  | 91 |  | 122
| Period of Outage | 1.8.2022 to 13.8.2022 |  |  |  | 15.04.2024 to 15.07.2024 |  | 01.4.2026 to 31.7.2026
| Reasons for Outage | LC no.284 issued to carry annual overhaul works |  |  |  | reconditioning of ventilation duct from ventilation room to Draft tube floor |  | Annual Overhauling of Unit-1
| No of days of outage | 1 |  |  |  | 122
| Period of Outage | 9.1.2023 |  |  |  | 01.4.2024 to 31.7.2024
| Reasons for Outage | Hand Tripped as per the request of AE/A&C for removing and testing of 2 Nos Batteries of 220 Volts Station batteries.After testing of 220 Volts Station batteries Unit taken into Service |  |  |  | Supply and installation for vibration meters and proximity sensors for both the units.
| No of days of outage | 1 |  |  |  | 122
| Period of Outage | 23.1.2023 |  |  |  | 01.4.2024 to 31.7.2024
| Reasons for Outage | Hand Tripped as per the request of AE/A&C for check the follow down limit relay of Excitation system |  |  |  | Emulsifier system for Generator transformer for Unit-1 &2
| No of days of outage |  |  |  |  | 122
| Period of Outage |  |  |  |  | 01.4.2024 to 31.7.2024
| Reasons for Outage |  |  |  |  | Installation of dedicated 132KV/11KV Transformer by creating additional bay at 132KV switchyard at NSLCPH.
B. | Forced Outages
| No of days of outage | 1
| Period of Outage | 14.10.2023
| Reasons for Outage | Unit tripped due to 86G3 & 86A relays operated
| No of days of outage | 1
| Period of Outage | 5.1.2023
| Reasons for Outage | Unit Tripped due to low Governor oil pressure.
2 | Unit 2
A. | Planned Outages
| No of days of outage | 16 | 148 |  |  | 91 | 122 |  | 122 | 122
| Period of Outage | 12.7.2022 to 28.7.2022 | 6.5.2023 to 1.10.2023 |  |  | 15.04.2024 to 15.07.2024 | 01.4.2025 to 31.7.2025 |  | 01.4.2027 to 31.7.2027 | 01.4.2028 to 31.7.2028
| Reasons for Outage | LC no.288 issued to carry annual overhaul works | PIG reconditioning works of unit 2 |  |  | Reconditioning & replacing of bulb seal for draft tube gates of unit-2 | Capital Overhauling of Unit-2 |  | AVR to DVR of Unit-2 | Annual Overhauling of Unit-2
| No of days of outage | 2 | 152 |  |  | 122
| Period of Outage | 7.12.2022 to 8.12.2022 | 6.5.2023 to 5.10.2023 |  |  | 01.4.2024 to 31.7.2024
| Reasons for Outage | Unit is not Taken into service Due to U-I Governor Problem. | PIG hydraulic cylinder reconditioning works of unit 2 |  |  | commisioning of new elctro hydraulic governor control panel for unit 2
| No of days of outage | 1
| Period of Outage | 9.1.2023
| Reasons for Outage | Hand Tripped as per the request of AE/A&C for removing and testing of 2 Nos Batteries of 220 Volts Station batteries.After testing of 220 Volts Station batteries Unit taken into Service
B. | Forced Outages
| No of days of outage | 1
| Period of Outage | 01.8.2022
| Reasons for Outage | Unit tripped due to 86G3 relay operated.
| No of days of outage | 1
| Period of Outage | 5.8.2022
| Reasons for Outage | Unit tripped due to 86G,86A, 86B&C and Generator O/F relay 81G/Generator U/V relays relays operated.
| No of days of outage | 1
| Period of Outage | 14.10.2022
| Reasons for Outage | Unit tripped due to 132KV BUS Dead at NSLC Power House,due to the opening of 132 KV LCPH - NSR feeders CB52 at 220KVRS and 132 KV LCPH - KM Pally feeder is already in tripped condition.
| No of days of outage | 1
| Period of Outage | 21.12.2022
| Reasons for Outage | Unit Tripped due to the failure of Transformer oil pumps - 1& 2
| No of days of outage | 1
| Period of Outage | 29.1.2023
| Reasons for Outage | Unit Tripped due to86G2,86A and 86 B&C relays(Excitation protection fault) operated.
| No of days of outage | 1
| Period of Outage | 27.2.2023
| Reasons for Outage | Unit tripped due to Reverse Power,86C relay operated
Note: | Details of outages should be submitted for each Unit of each station separately

## Table 13 (hidden)
<Name of the Generating Entity> <Name of the Generating Stations Form 9: Planned & Forced Outages

## Table 14 (hidden)
<Name of the Generating Entity>
<Name of the Generating Stations
Form 9: Planned & Forced Outages
S.No. | Particulars | Year (n-1) | Gurrent Year ’n’ |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | n+1 | n+2 | n+3 | n+4 | n+5
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
Unit 1 / Station 1
A. | Planned Outages
No of days of outage
Period of Outage
Reasons for Outage
B. | Forced Outages
No of days of outage
Period of Outage
Reasons for Outage
2 | Unit 2 / Station 2

## Table 15 (hidden)
Note: Details of outages should be submitted for each Unit of each station separately

## Table 16 (hidden)
<Name of the Generating Entity> <Name of the Generating Station> Form 1 : Plant Characteristics (Hydel)
1. Location
State/Distt.
River
2. Diversion Tunnel
Size, shape
Length
3. Dam
Type
Maximum dam height
4. Spillway
Type
Crest level of spillway
5. Reservoir
Full Reservior Level (FRL)
Minimum Oraw Down Level (MDDL)
Live storage (MCM)
6. Desilting Arrangement
Type
Number and Size
Particle size to be removed(mm)
7. Head Race Tunnel
Size and type
Length
Design discharge(Cumecs)
8. Surge Shaft
Type
Diameter
Height
9. Penstock/Pressure shafts
Type
Diameter & Length
10. Power House
Type
Installed capacity (No of units x MW)
Peaking capacity during lean period (MW)
Type of turbine
Rated Head(M)
Rated Discharge(Cumecs)
11. Tail Race Tunnel
Diameter, shape
Length
Minimum tail water level
12. Switchyard
Type of Switch gear
No. of generator bays
No. of Bus coupler bays
No. of line bays

## Table 17 (hidden)
Note: Specify limitation on generation during specific time period on account of restriction(s) on water use due to irrigation, drinking water, industrial, environmental considerations etc.