## U1
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit-1
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 1 / LJHEP
A. | Planned Outages
| No of days of outage | 8 | 8 | _ | 8 | 1)8 2)25 | 8 | 8 | 8 | 8
| Period of Outage | 13.04.2022 to 20.04.2022 | 13.04.2023 to 20.04.2023 | _ | 13.04.2023 to 20.04.2023 | 1)13.04.2024 to 20.04.2024 2)11.05.2024 to 04.06.2024 | 13.04.2025 to 20.04.2025 | 13.04.2026 to 20.04.2026 | 13.04.2027 to 20.04.2027 | 13.04.2028 to 20.04.2028
| Reasons for Outage | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | _ | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 0.625 (15:01:00 Hrs) | 0.059 (01:25) Hrs | 0 | 0.059 Day (01:25) Hrs
| Period of Outage | Details enclosed in Annexure-I | Details enclosed in Annexure-I
| Reasons for Outage | Details enclosed in Annexure-I | Details enclosed in Annexure-I
Note:
Details of outages should be submitted for each Unit of each station separately

## U2
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit-2
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 2 / LJHEP
A. | Planned Outages
| No of days of outage | 1)8 2)42.96 (1031:11 Hrs) | 8 | _ | 8 | 1)8 2)25 | 8 | 8 | 8 | 8
| Period of Outage | 1)21.04.2022 to 29.04.2022 2)19.08.2022 @00:00 hrs to 29.09.2022 @ 23:11 Hrs | 21.04.2023 to 29.04.2023 | _ | 21.04.2023 to 29.04.2023 | 1)21.04.2024 to 29.04.2024 2)05.06.2024 to 30.06.2024 | 21.04.2025 to 29.04.2025 | 21.04.2026 to 29.04.2026 | 21.04.2027 to 29.04.2027 | 21.04.2028 to 29.04.2028
| Reasons for Outage | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Under LC(Shaft seal rectification work) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | _ | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 0.845 (20:17 Hrs) | 0.169 (04:04 Hrs) | _ | 0.169 (04:04 Hrs)
| Period of Outage | Details enclosed in Annexure-II | Details enclosed in Annexure-II
| Reasons for Outage | Full details enclosed in Annexure-II | Full details enclosed in Annexure-II
Note:
Details of outages should be submitted for each Unit of each station separately

## U3
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit-3
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Sep | Oct-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 3 / LJHEP
A. | Planned Outages
| No of days of outage | 8 | 8 |  | 8 | 1)8 2)25 | 8 | 8 | 8 | 8
| Period of Outage | 30.04.2022 to 07.05.2022 | 30.04.2023 to 07.05.2023 | _ | 30.04.2023 to 07.05.2023 | 1)30.04.2024 to 07.05.2024 2)16.04.2024 to 10.05.2024 | 30.04.2025 to 07.05.2025 | 30.04.2026 to 07.05.2026 | 30.04.2027 to 07.05.2027 | 30.04.2028 to 07.05.2028
| Reasons for Outage | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | _ | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 0.52 (12:34 Hrs) | 1.132 (27:10) Hrs | _ | 1.132 (27:10) Hrs
| Period of Outage | Details enclosed in Annexure-III | Details enclosed in Annexure-III
| Reasons for Outage | Full details enclosed in Annexure-III | Full details enclosed in Annexure-III
Note:
Details of outages should be submitted for each Unit of each station separately

## U4
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit -4
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Oct | Nov-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 4 / LJHEP
A. | Planned Outages
| No of days of outage | 1) 0.485 2)0.94 3)8 | 8 | 10 | 1)8 2)10 | 1)15 2)8 | 8 | 8 | 8 | 8
| Period of Outage | 1)18.10.2022 @11:00 to 18.10.2022 @22:40(11:40 Hrs) 2)28.10.2022@ 22:45 to 29.10.2022 @21:13 (22:28 Hrs) 3)08.05.2022 to 15.05.2022 | 08.05.2023 to15.05.2023 | 22.03.2024 to 31.03.2024 | 1)08.05.2023 to15.05.2023 2)22.03.2024 to 31.03.2024 | 1)01.04.2024 to 15.04.2024 2)08.05.2024 to 15.05.2024 | 08.05.2025 to 15.05.2025 | 08.05.2026 to 15.05.2026 | 08.05.2027 to 15.05.2027 | 08.05.2028 to 15.05.2028
| Reasons for Outage | 1)Unit Deparalled for Shaft Seal Water leak rectification works(LC) 2)Unit Deparalled for Shaft Seal Water leak rectification works(LC) 3)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | 1)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) 2)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 0.74 (17:41 Hrs) | 0.234 (05:37) Hrs | _ | 0.234 (05:37) Hrs
| Period of Outage | Details enclosed in Annexure-IV | Details enclosed in Annexure-IV
| Reasons for Outage | Full details enclosed in Annexure-IV | Full details enclosed in Annexure-IV
Note:
Details of outages should be submitted for each Unit of each station separately

## U5
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit -5
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Oct | Nov-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 5 / LJHEP
A. | Planned Outages
| No of days of outage | 1)8 2)0.377 | 8 | 25 | 1)8 2)25 | 8 | 8 | 8 | 8 | 8
| Period of Outage | 1)16.05.2022 to 23.05.2022 2)11.10.2022 @17:55 to 12.10.2022 @02:59 (09:04 Hrs) | 16.05.2023 to 23.05.2023 | 26.02.2024 to 21.03.2024 | 1)16.05.2023 to 23.05.2023 2)26.02.2024 to 21.03.2024 | 16.05.2024 to 23.05.2024 | 16.05.2025 to 23.05.2025 | 16.05.2026 to 23.05.2026 | 16.05.2027 to 23.05.2027 | 16.05.2028 to 23.05.2028
| Reasons for Outage | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water 2)Unit Deparalled for Shaft Seal Water leak rectification works(LC) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 1.59 (38:07 Hrs) | 0.87 (20:58) Hrs | _ | 0.87 (20:58) Hrs
| Period of Outage | Details enclosed in Annexure-V | Details enclosed in Annexure-V
| Reasons for Outage | Full details enclosed in Annexure-V | Full details enclosed in Annexure-V
Note:
Details of outages should be submitted for each Unit of each station separately

## U6
TELANGANA POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 9: Planned & Forced Outages
Unit-6
S.No. | Particulars | Year 2022-23 | Current Year 2023-24 |  |  | Control Period
|  | April-March | Apr-Oct | Nov-Mar | Apr - Mar | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29
|  | Actual | Actual | Estimated | Estimated | Projected | Projected | Projected | Projected | Projected
1 | Unit 6 / LJHEP
A. | Planned Outages
| No of days of outage | 1)0.43 2)5.03 3)8 | 8 | 25 | 1)8 2)25 | 8 | 8 | 8 | 8 | 8
| Period of Outage | 1)21.10.2022 @11:00 to 21.10.2022 @21:22 (10:22 Hrs) 2)26.10.2022@10:32 to 31.10.2022@11:17 Hrs(120:45 Hrs) 3)24.05.2022 to 31.05.2022 | 24.05.2023 to 31.05.2023 | 01.02.2024 to 25.02.2024 | 1)24.05.2023 to 31.05.2023 2)01.02.2024 to 25.02.2024 | 24.05.2024 to 31.05.2024 | 24.05.2025 to 31.05.2025 | 24.05.2026 to 31.05.2026 | 24.05.2027 to 31.05.2027 | 24.05.2028 to 31.05.2028
| Reasons for Outage | 1)Unit Deparalled for Shaft Seal Water leak rectification works(LC) 2)Unit Deparalled for Shaft Seal Water leak rectification works(LC) 3)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | 1)Annual Overhaul (Units AOH will be taken up during non availabilty of water ) 2)Rectification of Shaft Seal problem by OEM ( Work will be taken up during non availabilty of water) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water ) | Annual Overhaul (Units AOH will be taken up during non availabilty of water )
B. | Forced Outages
| No of days of outage | 0.895 (21:30 Hrs) | 0.103 (02:29) Hrs | _ | 0.103 (02:29) Hrs
| Period of Outage | Details enclosed in Annexure-VI | Details enclosed in Annexure-VI
| Reasons for Outage | Full details enclosed in Annexure-VI | Full details enclosed in Annexure-VL
Note:
Details of outages should be submitted for each Unit of each station separately

## f18
TELANGANA STATE POWER GENERATION CORPORATION LIMITED
LOWER JURALA HYDRO ELECTRIC PROJECT
Form 18: Plant Characteristics (Hydel)
1. Location
State/Distt. | Telangana / Wanaparthy
River | Krishna
2. Diversion Tunnel
Size, shape | Trapezoidal(Lined)
Length | 1.723 Km
3. Dam
Type | Weir (over flow)
Maximum dam height | EL + 299M
4. Spillway
Type | over flow
Crest level of spillway | EL + 299M
5. Reservoir
Full Reservior Level (FRL) | 299.00 M
Minimum Draw Down Level (MDDL) | 296.5 M
Live storage (MCM) | 8.49
6. Desilting Arrangement
Type | Vertical gates
Number and Size | 2, 6 X 3M
Particle size to be removed(mm) | _
7. Head Race Tunnel
Size and type | 115M (width), Trapezoidal
Length | 263 mtrs
Design discharge(Cumecs) | 1440
8. Surge Shaft
Type | _
Diameter | _
Height | _
9. Penstock/Pressure shafts
Type | _
Diameter & Length | _
10. Power House
Type | Surface Power House
Installed capacity (No of units x MW) | 6 x 40 MW
Peaking capacity during lean period (MW) | _
Type of turbine | Bulb type
Rated Head(M) | 20.0 M
Rated Discharge(Cumecs) | 240 m3/Sec (8475 cusecs) by each unit
11. Tail Race Tunnel
Diameter, shape | Trapezoidal (unlined)
Length | 1920 M.
Minimum tail water level | 273.65 M(One Unit in operation)
12. Switchyard
Type of Switch gear | OUT DOOR
No. of generator bays | 6
No. of Bus coupler bays | 1
No. of line bays | 4
Note: Specify limitation on generation during specific time period on account of restriction(s) on
water use due to irrigation, drinking water, industrial, environmental considerations etc.

## U1 details
LJHEP U #1 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 14.07.2022 | 10:19 | 14.07.2022 | 12:47 | 2:28 | Unit tripped on Governor header circuit pressure too low due to governor main pump coupling bolt broken.
2 | 07.08.2022 | 18:52 | 07.08.2022 | 19:25 | 0:33 | Unit tripped on controller watchdog fault
3 | 07.08.2022 | 22:04 | 07.08.2022 | 22:12 | 0:08 | Unit deparalled due to abnormal sound at distributor ring
4 | 08.08.2022 | 8:14 | 08.08.2022 | 9:00 | 0:46 | Unit tripped on controller watchdog fault
5 | 08.08.2022 | 9:05 | 08.08.2022 | 9:37 | 0:32 | Unit tripped on excitation controller fault
6 | 20.08.2022 | 10:20 | 20.08.2022 | 18:08 | 7:48 | Unit deparalled for lowering of DT elements of Unit # 2
7 | 26.08.2022 | 4:33 | 26.08.2022 | 6:03 | 1:30 | Unit tripped on over frequency, due to 220KV veltoor Line1 # Line 2 tripping & bus dead
8 | 30.08.2022 | 11:40 | 30.08.2022 | 12:06 | 0:26 | Unit deparalled due to Governor controller hang
9 | 21.09.2022 | 13:40 | 21.09.2022 | 14:30 | 0:50 | Unit Deparlleled for removing Dead body in intake pool
Total |  |  |  |  | 15:01
LJHEP U #1 Forced Outage From April 2023 to Sep-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 27.07.2023 | 5:28 | 27.07.2023 | 6:05 | 0:37 | Unit Tripped on Excitation fault
2 | 31.07.2023 | 17:55 | 31.07.2023 | 18:09 | 0:14 | Unit deparalled to clear the trash in the intake pool
3 | 04.08.2023 | 1:52 | 04.08.2023 | 2:09 | 0:17 | Unit deparalled to clear the trash at intake pool
4 | 09.09.2023 | 8:28 | 09.09.2023 | 8:45 | 0:17 | Unit tripped on Generator stator winding temperature signal RTD malfunction
Total |  |  |  |  | 1:25
LJHEP U #1 Forced Outage From Oct 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00

## U2 details
LJHEP U #2 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 16.07.2022 | 19:46 | 16.07.2022 | 22:36 | 2:50 | Unit Tripped on Buchholz relay operated due to GSU oil level low (GSU Cooler leakage).
2 | 23.07.2022 | 0:00 | 23.07.2022 | 10:23 | 10:23 | Unit deparalled for GSU cooler rectification works.
3 | 15.08.2022 | 11:00 | 15.08.2022 | 11:23 | 0:23 | Unit tripped on controller watchdog fault
4 | 18.08.2022 | 17:19 | 19.08.2022 | 0:00 | 6:41 | Unit deparalled due to Shaft seal water leakage
Total |  |  |  |  | 20:17
LJHEP U #2 Forced Outage From April 2023 to Sep-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 05.08.2023 | 11:55 | 05.08.2023 | 14:45 | 2:50 | Unit tripped due to Stator earth fault protection 95% relay operated
2 | 11.09.2023 | 20:07 | 11.09.2023 | 21:21 | 1:14 | Unit tripped on generator cooler fans (2 & 5) fault
Total |  |  |  |  | 4:04
LJHEP U #2 Forced Outage From Oct 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00

## U3 details
LJHEP U #3 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 14.07.2022 | 13:26 | 14.07.2022 | 13:42 | 0:16 | Unit tripped on Carbon dust exhauster off (contact cable loose connection)
2 | 31.07.2022 | 4:15 | 31.07.2022 | 4:53 | 0:38 | Unit Tripped due to feeder-I external fault.
3 | 02.08.2022 | 6:45 | 02.08.2022 | 6:57 | 0:12 | Unit tripped on excitation fault due to thirstier bridge over temperature
4 | 26.08.2022 | 4:33 | 26.08.2022 | 6:13 | 1:40 | Unit tripped on over frequency, due to 220KV veltoor Line1 # Line 2 tripping & bus dead
5 | 14.09.2022 | 17:57 | 14.09.2022 | 19:34 | 1:37 | Controller watch dog(TSLG) fault
6 | 14.09.2022 | 19:58 | 14.09.2022 | 21:23 | 1:25 | Controller watch dog(TSLG) fault
7 | 14.09.2022 | 21:31 | 14.09.2022 | 24:00 | 2:29 | Controller watch dog(TSLG) fault
8 | 15.09.2022 | 0:00 | 15.09.2022 | 0:16 | 0:16 | Controller watch dog(TSLG) fault
9 | 15.09.2022 | 3:26 | 15.09.2022 | 5:44 | 2:18 | MFC Change over Failure
10 | 15.09.2022 | 22:46 | 15.09.2022 | 23:40 | 0:54 | Governor communication fault
11 | 21.09.2022 | 13:44 | 21.09.2022 | 14:33 | 0:49 | Unit Deparlleled for removing Dead body in intake pool
Total |  |  |  |  | 12:34
LJHEP U # 3 Forced Outage From April 2023 to Sep-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
| 30.07.2023 | 15:36 | 30.07.2023 | 17:59 | 2:23 | Unit deparalled on Governor oil sump Temperature high
| 30.07.2023 | 23:45 | 31.07.2023 | 2:11 | 2:26 | Unit deparalled on Governor Temperature high
| 31.07.2023 | 7:23 | 31.07.2023 | 13:38 | 6:15 | Unit deparalled on Governor Temperature high
| 04.08.2023 | 17:07 | 04.08.2023 | 17:27 | 0:20 | Unit deparalled to clear the trash at intake pool
| 06.09.2023 | 9:48 | 07.09.2023 | 1:34 | 15:46 | Unit deparalled due to Shaft Seal water leak
Total |  |  |  |  | 27:10
LJHEP U # 3 Forced Outage From Oct 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00

## U4 details
LJHEP U #4 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 20.07.2022 | 23:52 | 21.07.2022 | 1:01 | 1:09 | Unit Tripped on Generator RTD malfunction.
2 | 20.08.2022 | 2:11 | 20.08.2022 | 3:56 | 1:45 | Unit tripped on controller watchdog fault
3 | 26.08.2022 | 4:33 | 26.08.2022 | 5:56 | 1:23 | Unit tripped on over frequency, due to 220KV veltoor Line1 # Line 2 tripping & bus dead
4 | 01.09.2022 | 1:09 | 01.09.2022 | 11:38 | 10:29 | Unit Deparalled due to Shaft Seal Water leak
5 | 20.09.2022 | 18:17 | 20.09.2022 | 19:42 | 1:25 | MFC Change over Failure
6 | 21.09.2022 | 13:49 | 21.09.2022 | 15:19 | 1:30 | Unit Deparlleled for removing Dead body in intake pool
Total |  |  |  |  | 17:41
LJHEP U # 4 Forced Outage From April 2023 to Oct-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
| 01.08.2023 | 10:41 | 01.08.2023 | 10:51 | 0:10 | Unit deparalled to clear the trash at intake pool
| 11.08.2023 | 20:35 | 11.08.2023 | 21:30 | 0:55 | unit tripped on lubrication system fault
| 06.09.2023 | 0:33 | 06.09.2023 | 1:02 | 0:29 | Unit deparalled due to Circuit Breaker DC Supply-I failure
| 01.10.2023 | 19:16 | 01.10.2023 | 22:32 | 3:16 | Unit tripped due to SAT- 1 & 3 supply failure.
| 03.10.2023 | 12:58 | 03.10.2023 | 13:45 | 0:47 | Unit tripped on controller watchdog fault
Total |  |  |  |  | 5:37
LJHEP U # 4 Forced Outage From Nov 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00

## U5 details
LJHEP U #5 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 31.07.2022 | 4:15 | 31.07.2022 | 5:04 | 0:49 | Unit Tripped on SAT-3 Incomer fault(feeder-I external fault).
2 | 04.08.2022 | 16:57 | 05.08.2022 | 1:48 | 8:51 | Unit deparalled for shaft seal rectification works
3 | 26.08.2022 | 4:33 | 26.08.2022 | 6:32 | 1:59 | Unit tripped on over frequency, due to 220KV veltoor Line1 & Line 2 tripping & bus dead
4 | 21.09.2022 | 13:46 | 21.09.2022 | 14:54 | 1:08 | Unit Deparlleled for removing Dead body in intake pool
5 | 01.10.2022 | 0:00 | 01.10.2022 | 20:45 | 20:45 | Unit Deparlleled due to lub Oil pumps abnormal sound
6 | 02.10.2022 | 9:10 | 02.10.2022 | 13:28 | 4:18 | Unit Deparlleled due to lub Oil pumps abnormal sound
7 | 19.10.2022 | 16:38 | 19.10.2022 | 16:55 | 0:17 | Unit Deparalled to clear trash at trash racks of intake gates
Total |  |  |  |  | 38:07
LJHEP U #5 Forced Outage From April 2023 to Sep-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
| 23.07.2023 | 15:20 | 24.07.2023 | 0:54 | 9:34 | Unit tripped on lube oil level too low
| 01.08.2023 | 15:53 | 01.08.2023 | 16:27 | 0:34 | Unit deparalled to clear the trash at intake pool
| 08.08.2023 | 11:40 | 08.08.2023 | 22:30 | 10:50 | Unit deparalled to arrest shaft seal water leak
Total |  |  |  |  | 20:58
LJHEP U # 5 Forced Outage From Oct 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00

## U6 details
LJHEP U #6 Forced Outage From April 2022 to March-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | 16.07.2022 | 23:45 | 17.07.2022 | 0:04 | 0:19 | Unit tripped on Generator counter thrust bearing pad temp high (RTD malfunction).
2 | 31.07.2022 | 4:15 | 31.07.2022 | 4:48 | 0:33 | Unit Tripped on SAT-3 Incomer fault(feeder-I external fault).
3 | 06.08.2022 | 17:52 | 06.08.2022 | 18:34 | 0:42 | Unit deparalled for checking GSU T/F oil level and for top up
4 | 26.08.2022 | 4:33 | 26.08.2022 | 6:49 | 2:16 | Unit tripped on over frequency, due to 220KV veltoor Line1 & Line 2 tripping & bus dead
5 | 29.08.2022 | 11:40 | 29.08.2022 | 12:08 | 0:28 | Unit Tripped on TSLG fault due to communication failure
6 | 29.08.2022 | 12:11 | 29.08.2022 | 12:19 | 0:08 | Unit Tripped on Governor supply failure
7 | 30.08.2022 | 10:34 | 30.08.2022 | 23:19 | 12:45 | Unit deparalled due to shaft seal water leakage
8 | 01.09.2022 | 22:16 | 01.09.2022 | 22:50 | 0:34 | Unit tripped on controller watchdog fault
9 | 05.09.2022 | 21:58 | 05.09.2022 | 23:40 | 1:42 | Unit tripped on controller fault
10 | 07.09.2022 | 21:48 | 07.09.2022 | 22:53 | 1:05 | Unit Deparalled for controller program loading
11 | 21.09.2022 | 13:46 | 21.09.2022 | 14:37 | 0:51 | Unit Deparlleled for removing Dead body in intake pool
12 | 24.09.2022 | 21:14 | 24.09.2022 | 21:21 | 0:07 | Deparlleled due to Swirling effect in intake pool
Total |  |  |  |  | 21:30
LJHEP U #6 Forced Outage From April 2023 to Sep-2023
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
| 08.08.2023 | 8:13 | 08.08.2023 | 9:42 | 1:29 | Unit tripped on excitation fault
| 10.09.2023 | 1:45 | 10.09.2023 | 2:45 | 1:00 | Unit tripped on TSLG governor fault
Total |  |  |  |  | 2:29
LJHEP U # 6 Forced Outage From Oct 2023 to Mar-2024
Si No | Forced Outage |  |  |  |  | Brief description Planed, Forced / Misc. outage & remarks
| Start |  | End |  | Total Hrs:min
| Date | Time | Date | Time
1 | NIL |  |  |  | 0:00
Total |  |  |  |  | 0:00